## Slide 1: Energy measurement
Energy efficient infrastructure
Bart Van der Spiegel
Energy Management bart.vanderspiegel@infrabel.be
2 July 2018

## Slide 2
Production
Transmission
Distribution
Consumptions
Traction-energy:
Energy consumption of trains
(Railway Undertakings)
‘Traction’-contract:
65 connections on transmission network of Elia (88 %)
20 connections to distribution networks (12 %)
‘Distribution’-contract: 1400 connections to distribution networks
1350 GWh
130 GWh
140 GWh
Distribution-energy:
Energy for electrical installations of Infrabel, SNCB and third parties (signalling, switch heating, platform lighting, stations, maintenance shops, etcetera).
Purchasing by Infrabel
2

## Slide 3
Automatic import of consumptions

## Slide 4
Reporting in graphs and reports (possible by day, by interval and by month)

## Slide 5
Parameters for supply point (versions with start and end time)

## Slide 6
6
Invoice verification for each EAN and for each consumption period.
Invoice details regarding distribution
Invoice simulation regarding distribution

## Slide 7
7
16 kW
From sunset to sunrise
Cost allocation to e.g. platform lighting

## Slide 8
8
Formula for virtual meter (versions possible)

## Slide 10
230 kW
Cost allocation to switch heating
Positive temperature and now snow
Cold, temperature regulated
Snow, continuously on

## Slide 11
Complex formula allocates this consumption to switch heating

## Slide 12
12
Tele-measured sub-metering point: via datalogger, meter with integrated datalogger and via own supervision systems

## Slide 13: When do we need a submeter?
substation
MV
station
maintenance shop SNCB
signalling
MV
LV
LV
signalling
building
MV
LV
station
switch heating
signalling
telemeasured

## Slide 14: Example 1: EDMI of Steel
Eziview
EIServer
TCP-IP
Moxa

## Slide 15: Example 2: NSX, PM and iEM of Schneider
Kies iEM3x55 indien bidirectionele stroommeting nodig is.
24 V DC supply : ABL7RM24025
* Micrologic E op NSX only has a sufficient accuracy starting from 10% of nominal current
Struxureware Power Monitoring Expert
EIServer

## Slide 16: Example 3: with a datalogger
Up to 32 energy meters: with potential free pulses
Also possible to connect meters via Modbus with RTU
Energy management system Infrabel

## Slide 17: Example 4: supervision system as datalogger
  Supervision system collects every 15’ the data consumption
  Every night a file with consumptions of previous day is exported
  EIServer collects CSV-file from FTP-server
Format:
HAS_TRPAO 15 Q415/A+,20141105 00:00,2,9.5,1
HAS_TRPAO 15 Q415/A+,20141105 00:15,2,11.0,1
HAS_TRPAO 15 Q415/A+,20141105 00:30,2,8.4,1
Element | Explanation
Name | unique ID for channal
Date and time | date and time at end of measurement period (different formats possible)
Offset | the offset of time to UTC (2 hours in summer and 1 hour in winter)
Value | consumption (in kWh)
Quality | can be used to give a quality code of the measured value

## Slide 18
?
QUESTIONS